## Single Line
SKU Number: | [9 empty] | System Type: |  | Gutor PXP 1010-400/230-EN-R
earth bar
| I byp |  | 45.3 |  |  | 10 mm2 |  |  |  | I byp_out | 43.48 |  | 10 mm2 |  |  |  | 20x6 mm
earth T501
16 mm2
43.48
[6 empty] | earth T001 | [8 empty] | earth T401
[6 empty] | 16 mm2 | [8 empty] | 16 mm2
| I in | [9 empty] | I BatCable | [6 empty] | I out
| 35.42 |  | 10 mm2 | [7 empty] | 26.31 |  | 6 mm2 |  |  |  |  | 43.48 | 10 mm2
|  |  | Input |  | Bypass |  | Output
| Transf. |  | Yes |  | Yes |  | Yes |  | UBatInitial | 449.5 | IBatNom | 22.37 |  | Temp. version: |  | 4
| Voltage |  | 230 |  | 230 |  | 230 |  | UBatBoost | 449.5 | IBatMax | 39.47 |  | Conf. version: |  | V8.6.2.4.3
| Phase(s) |  | 3 ph |  | 1 |  | 1 |  | UBatFloat | 449.5 | IBatCharge | 6.8 |  | Date/Initials:
| Frequency |  | 60 Hz |  |  |  | 60 Hz |  | UBatNom | 396
| Power | [5 empty] | 10 |  | UBatDis | 336.6 |  |  |  | Signature:
Rev |  | Date |  | Who |  |  | Description
1 |  |  |  | THA |  |  | initial
2 |  | 2008-07-22 |  | THA |  |  | fields for earth T001, T501, T401 and earth bar added
3 |  | 2009-03-13 |  | SKI |  |  | added "Configurator version" field in cell AI33
4 |  | 2013-12-04 |  | JPE |  |  | changed layout to support general graphical report layout for BM release 8.2.2.3.1
10

## Cabinet
SKU Number: | [9 empty] | System Type: |  |  | PXP 1010-400/230-EN-R
Bypass / Coupling
|  |  | UPS 1 |  | UPS 1 |  | Trafo 1 | Incoming 1 |  |  | UPS 2 | UPS 2 |  | Trafo 2 | Incoming 2 |  | Distribution
| Length: |  | 600 |  | 0 |  | 0 | 0 |  |  | 600 | 0 |  | 0 | 0 | 400 | 0
| Weight: |  |  |  | 440 | [6 empty] | 440 |  |  |  | 160 | 0
| Height: | [7 empty] | 2000 | [7 empty] | 0
[16 empty] | Template version: |  | 2
Configurator version:
| Total Cabinet Length: | [7 empty] | 1600 |  |  |  |  | Date/Initials:
| Total Cabinet Depth: | [7 empty] | 800
| Total Cabinet Weight: | [7 empty] | 1040 |  |  |  |  | Signature:
Rev |  | Date |  | Who |  | Description
1 |  |  |  | THA |  | initial
2 |  | 2009-03-13 |  | SKI |  | added "Configurator version" field in cell AJ32
10

## Single Line->internal use only! (hidden)
SKU Number: | [9 empty] | System Type: | [15 empty] | Cable Dimensions |  | Earth Cable Dimensions |  | Earth Bar Dimensions |  | Input Transformer |  |  |  |  | Output Transformer
[21 empty] | Constants | [10 empty] | 190 | 190 | 0.45894 | 414 | 414 | 414 | 414 | 0.45894 | 190 | 190
| I byp (L2) |  | 836.7395 |  |  | 3x120 mm2 | [9 empty] | earth bar |  |  |  |  | Efficiency_Inverter | 97% |  |  |  | mm2 | A | mm2 | A | Cu | A | 200 | 208 | 0.50242 | 398.0769 | 414 | 398.0769 | 414 | 0.50242 | 200 | 208
| I byp (L1,L3) |  | 418.3698 |  |  | 2x70 mm2 |  |  |  | I byp_out | 727.2727 |  | 2x150 mm2 |  |  | 2x20x6 mm |  |  |  |  | Efficiency_Rectifier | 97% |  |  |  | 6 mm2 | 1 | 16 mm2 | 1 | 20x6 mm | 1 | 220 | 230 | 0.55556 | 396 | 414 | 396 | 414 | 0.55556 | 220 | 230
[8 empty] | earth T501 | [12 empty] | Efficiency_Input_Trafo | 96% |  |  |  | 6 mm2 | 43 | 16 mm2 | 139 | 20x6 mm | 638 | 380 | 380 | 0.91787 | 414 | 414 | 414 | 414 | 0.91787 | 380 | 380
[8 empty] | 95 mm2 | [12 empty] | Efficiency_Output_Trafo | 96% |  |  |  | 10 mm2 | 62 | 50 mm2 | 271 | 2x20x6 mm | 1016 | 400 | 415 | 1.0024 | 399.0361 | 414 | 399.0361 | 414 | 1.0024 | 400 | 415
[21 empty] | Efficiency_Bypass_Trafo | 96% |  |  |  | 16 mm2 | 82 | 95 mm2 | 542 | 40x8 mm | 1476 | 440 | 440 | 1.0628 | 414 | 414 | 414 | 414 | 1.0628 | 440 | 440
[21 empty] | Minimal_Battery_Voltage | 335 |  |  |  | 25 mm2 | 112 | 2x95 mm2 | 1084 | 2x40x8 mm | 2952 | 460 | 480 | 1.1594 | 396.75 | 414 | 396.75 | 414 | 1.1594 | 460 | 480
[21 empty] | Output_Powerfactor | 0.8 |  |  |  | 35 mm2 | 139 | 3x95 mm2 | 2168 | n/a | 5000 | 500 | 525 | 1.2681 | 394.2857 | 414 | 394.2857 | 414 | 1.2681 | 500 | 525
[21 empty] | Maximal Battery Voltage | 451 |  |  |  | 50 mm2 | 178 | n/a | 5000 |  |  | 600 | 600 | 1.4493 | 414 | 414 | 414 | 414 | 1.4493 | 600 | 600
[21 empty] | BypassTransformer | delta |  |  |  | 70 mm2 | 224 |  |  |  |  | 660 | 690 | 1.6667 | 396 | 414 | 396 | 414 | 1.6667 | 660 | 690
[21 empty] | Wiring | mm2 |  |  |  | 95 mm2 | 271
[5 empty] | 214.4504 | [7 empty] | 760.6723 | [7 empty] | Imax for earth bar calculation | 727.2727 |  | Yes | No | 120 mm2 | 319 | [9 empty] | 219.1044 | 239.023 | 0.50204 | 110 | 120
[21 empty] | Rectifier Input Voltage | 399.0361 | 1.0024 | 50 | 60 | 150 mm2 | 369 | [9 empty] | 239.023 | 239.023 | 0.53133 | 127 | 127
[21 empty] | Inverter Output Voltage | 219.1044 | 1.0041 | 1 | 3 | 2x70 mm2 | 423 | [9 empty] | 219.1044 | 239.023 | 1.0041 | 220 | 240
[26 empty] | 2x95 mm2 | 542 | [9 empty] | 219.1763 | 239.023 | 1.1589 | 254 | 277
[26 empty] | 2x120 mm2 | 638 | [9 empty] | 239.023 | 239.023 | 1.2091 | 289 | 289
[26 empty] | 2x150 mm2 | 738
[15 empty] | 727.2727 | [10 empty] | 3x120 mm2 | 957 | [5 empty] | copied from the 430-0456-XXX_REV05 (Additional Information).xls file
[26 empty] | 3x150 mm2 | 1107
[26 empty] | 4x120 mm2 | 1276 | [5 empty] | 3 Phase Transformer |  |  |  |  | 1 Phase Transformer
[26 empty] | 4x150 mm2 | 1476
[6 empty] | earth T001 | [8 empty] | earth T401 | [10 empty] | 5x120 mm2 | 1595 | [5 empty] | 190 | 0.45894 |  |  |  | 110 | 0.50204
[6 empty] | 50 mm2 | [8 empty] | 2x95 mm2 | [10 empty] | 5x150 mm2 | 1845 | [5 empty] | 200 | 0.50242 |  |  |  | 115 | 0.50204
[26 empty] | 6x120 mm2 | 1914 | [5 empty] | 208 | 0.50242 |  |  |  | 120 | 0.50204
[26 empty] | 6x150 mm2 | 2214 | [5 empty] | 220 | 0.55556 |  |  |  | 127 | 0.53133
[26 empty] | n/a | 5000 | [5 empty] | 230 | 0.55556 |  |  |  | 220 | 1.0041
| I in | [9 empty] | I BatCable | [5 empty] | I out | [15 empty] | 380 | 0.91787 |  |  |  | 230 | 1.0041
| 222.8475 |  | 70 mm2 | [7 empty] | 409.5615 |  | 2x70 mm2 |  |  |  | 727.2727 | 2x150 mm2 | [14 empty] | 400 | 1.0024 |  |  |  | 240 | 1.0041
[33 empty] | 415 | 1.0024 |  |  |  | 254 | 1.1589
|  |  | Input |  | Bypass |  | Output | [25 empty] | 440 | 1.0628 |  |  |  | 277 | 1.1589
| Transf. |  | Yes |  | Yes |  | Yes |  | UBatInitial | 451 | IBatNom | 92 | [20 empty] | 460 | 1.1594 |  |  |  | 289 | 1.2091
| Voltage |  | 400 |  | 230 |  | 220 |  | UBatBoost | 442 | IBatMax | 154 | [6 empty] | Rev | 3 | [12 empty] | 480 | 1.1594
| Phase(s) |  | 3ph |  | 3 |  | 1 |  | UBatFloat | 430 | IBatCharge | 14 |  | Date/Initials: | [18 empty] | 500 | 1.2681
| Frequency |  | 60 |  |  |  | 50 |  | UBatNom | 384 | [22 empty] | 525 | 1.2681
| Power | [5 empty] | 160 |  | UBatDis | 346 |  |  |  | Signature: | [18 empty] | 600 | 1.4493
[33 empty] | 660 | 1.6667
Rev |  | Date |  | Who |  |  | Description | [25 empty] | 690 | 1.6667
1 |  |  |  | THA |  |  | initial
2 |  | 2008-07-22 |  | THA |  |  | fields for earth T001, T501, T401 and earth bar added, new values for diameter added
3 |  | 2009-08-11 |  | LOA |  |  | update with the actual transformer
10
1
2
5
7
9
9